DEPARTMENT HEAD REPORT

WASTEWATER TREATMENT PLANT

|  |  |  |
| --- | --- | --- |
|  | August 2018 | August 2019 |
| GALLONS TREATED | 12.744 MG | 15.749 MG |
| AVERAGE GALLONS TREATED | 0.411 MGD | 0.508 MGD |
| LABORATORY TESTS PERFORMED | 328 | 328 |
| MONTHLY REPORTS | 01 | 01 |
| RAIN FALL | 1.11 INCHES | 3.51 INCHES |
| RAIN FALL TO DATE | 22.75 INCHES | 39.74 INCHES |

|  |  |  |
| --- | --- | --- |
|  | PERMIT PARAMETERS | REPORTED |
| CBOD5/avg | 10.0 mg/L | 2.00 |
| CBOD5/max | 25.0 mg/L | 2.00 |
| CBOD5/lbs/day | 167.0 | 9.23 |
| TSS/avg | 15.0 mg/L | 1.58 |
| TSS/max | 40.0 mg/L | 3.50 |
| TSS/lbs/day | 250.0 | 7.58 |
| NH3-N/avg | 2.0 mg/L | 0.100 |
| NH3-N/max | 7.0 mg/L | 0.100 |
| NH3-N/lbs/day | 33.0 | 0.461 |
| D.O. minimum | 4.0 mg/L | 5.60 |
| pH minimum | 6.0 standard units | 7.08 |
| pH maximum | 9.0 standard units | 7..26 |
| E. coli avg | 126 colonies per 100 mil | 0.211 |
| E. coli 7dy/avg | 394 colonies per 100 mil | 0.839 |
| 2 Hour Peak Flow |  | 2479 gpm |
| Copper/avg |  | 22.1 ug/L |