DEPARTMENT HEAD REPORT

WASTEWATER TREATMENT PLANT

|  |  |  |
| --- | --- | --- |
|  | January 2021 | January 2022 |
| GALLONS TREATED | 29.813 MG | 13.10 MG |
| AVERAGE GALLONS TREATED |  0.962 MGD | 0.423 MGD |
| LABORATORY TESTS PERFORMED | 328 | 328 |
| MONTHLY REPORTS | 01 | 01 |
| RAIN FALL | 5.47 INCHES |  0.84 INCHES  |
| RAIN FALL TO DATE | 5.47 INCHES | 0.84 INCHES |

|  |  |  |
| --- | --- | --- |
|  | PERMIT PARAMETERS | REPORTED |
| CBOD5/avg | 10.0 mg/L | 2.93 |
| CBOD5/max | 25.0 mg/L | 4.91 |
| CBOD5/lbs/day | 167.0 | 10.9 |
| TSS/avg | 15.0 mg/L | 6.5 |
| TSS/max | 40.0 mg/L | 15.0 |
| TSS/lbs/day | 250.0 | 24.3 |
| NH3-N/avg | 2.0 mg/L | 0.100 |
| NH3-N/max | 7.0 mg/L | 0.100 |
| NH3-N/lbs/day | 33.0 | 0.366 |
| D.O. minimum | 4.0 mg/L | 8.40 |
| pH minimum | 6.0 standard units | 6.74 |
| pH maximum | 9.0 standard units | 7.23 |
| E. coli avg | 126 colonies per 100 mil | .420 |
| E. coli 7dy/avg | 394 colonies per 100 mil | .561 |
| 2 Hour Peak Flow | 4167 gpm | 948 gpm |
| Copper/avg |  | 0.016 mg/L |