**PUBLIC WORKS**

**November (10/22-11/20)**

**Wastewater**

* Normal ground maintenance & lab work.
* The blowers and grit machine at the headworks offline due to mechanical failure and finally able to fix it and get everything at the headworks operational.
* Going throughout the plant and fixing old faucets and leaks.
* The belt press has new doctor blades installed.
* Fallen trees at the outfall were removed from the creek.
* Sink holes and soil erosion due to the rain are being filled and taken care of.
* The baffle in the UV trough was filled with concrete as it was allowing water to bypass UV treatment, working with engineer to address the issues with the UV system.
* All the UV panels were pulled, and every bulb was cleaned manually.
* Clarifier 2 was taken out of service and once dried it will be caulked along the v-notch weir.
* Aerzen blower filters for the aeration basin were all pulled, cleaned, and re-installed.